## Scenario Guide
IO SIGNAL SUDOKU — Industrial I/O Allocation Platform
DEMO SCENARIO DATASET: Scenario C: Engineering Constraint Conflict
SCENARIO OVERVIEW
Safety conflict fixture (46 loops). Hazardous Zone 0 Ex-ia transmitter PT-FLARE-IS is locked to standard non-IS baseplate BP-01, triggering CP-SAT infeasibility and IEC 60079-11 physical barrier violation.
Platform Target | Emerson DeltaV Electronic Marshaling Cabinet CAB-01 (64 CHARMs)
Optimization Engine | Google OR-Tools CP-SAT v9.10+ (Constraint Programming)
Independent Validator | IEC 61131-2, IEC 60079-11 (Ex-ia), IEEE 518 Noise Segregation
Data Origin | SYNTHETIC DEMO BENCHMARK — Clearly labeled for hackathon evaluation
Signal Count | 46 instrumentation loops in this register

## Signal Register
tag | description | signal_type | voltage | is_intrinsic_safety | safety_integrity_level | multicore_cable_id | cable_pair_index | power_dissipation_watts | locked | assigned_position_id
PT-FLARE-IS | Flare Stack Toxic Gas Purge Pressure [Hazardous Zone 0 Ex-ia] | IS_AI_HART | 24VDC | TRUE | SIL-3 | CBL-999-HAZ | 1 | 0.85 | TRUE | BP-01-CH-01
PT-101 | Deethanizer Reboiler Pressure Transmitter | AI_HART | 24VDC | FALSE | BPCS | CBL-101A | 1 | 0.85 | FALSE | BP-01-CH-01
PT-102 | Separator Column Head Pressure | AI_HART | 24VDC | FALSE | BPCS | CBL-101A | 2 | 0.8 | FALSE | BP-01-CH-02
PT-103 | Boiler Drum Steam Pressure | AI_HART | 24VDC | FALSE | BPCS | CBL-101A | 3 | 0.8 | FALSE | BP-01-CH-03
LT-201 | Deethanizer Bottom Liquid Level | AI_HART | 24VDC | FALSE | BPCS | CBL-101A | 4 | 0.75 | FALSE | BP-01-CH-04
LT-202 | Reflux Drum Liquid Level | AI_HART | 24VDC | FALSE | BPCS | CBL-102A | 1 | 0.75 | FALSE | BP-01-CH-05
FT-301 | Crude Feed Orifice Flowmeter | AI_HART | 24VDC | FALSE | BPCS | CBL-102A | 2 | 0.9 | FALSE | BP-01-CH-06
FT-302 | Reflux Line Flow Transmitter | AI_HART | 24VDC | FALSE | BPCS | CBL-102A | 3 | 0.9 | FALSE | BP-01-CH-07
FT-303 | Steam Header Mass Flowmeter | AI_HART | 24VDC | FALSE | BPCS | CBL-102A | 4 | 0.9 | FALSE | BP-01-CH-08
FV-101 | Reflux Control Valve Positioner AO | AO_HART | 24VDC | FALSE | BPCS | CBL-103A | 1 | 0.95 | FALSE | BP-01-CH-09
PV-102 | Steam Bypass Valve Positioner AO | AO_HART | 24VDC | FALSE | BPCS | CBL-103A | 2 | 0.95 | FALSE | BP-01-CH-10
LV-201 | Bottoms Drain Control Valve AO | AO_HART | 24VDC | FALSE | BPCS | CBL-103A | 3 | 0.95 | FALSE | BP-01-CH-11
PT-104 | Cooling Water Return Pressure | AI_HART | 24VDC | FALSE | BPCS | CBL-103A | 4 | 0.75 | FALSE | BP-01-CH-12
PT-105-IS | Reactor Flare Header Pressure [Zone 0 Ex-ia] | IS_AI_HART | 24VDC | TRUE | SIL-2 | CBL-201A | 1 | 0.85 | TRUE | BP-02-CH-01
PT-106-IS | Hydrogen Purge Header Pressure [Zone 0 Ex-ia] | IS_AI_HART | 24VDC | TRUE | SIL-2 | CBL-201A | 2 | 0.85 | FALSE | BP-02-CH-02
FT-104B | Backup Boiler Feedwater Flow Transmitter [Zone 1] | IS_AI_HART | 24VDC | TRUE | SIL-2 | CBL-201A | 3 | 0.9 | FALSE | BP-02-CH-03
LT-205-IS | Hydrocarbon Slop Tank Level [Zone 1 Ex-ia] | IS_AI_HART | 24VDC | TRUE | SIL-2 | CBL-201A | 4 | 0.8 | FALSE | BP-02-CH-04
PT-107-IS | Polymer Flash Vessel Pressure [Zone 0 Ex-ia] | IS_AI_HART | 24VDC | TRUE | SIL-2 | CBL-202A | 1 | 0.85 | FALSE | BP-02-CH-05
ZS-201-IS | Emergency Blowdown Valve Position Switch [Ex-ia] | IS_DI_NAMUR | 24VDC | TRUE | SIL-2 | CBL-202A | 2 | 0.45 | FALSE | BP-02-CH-06
ZS-202-IS | Reactor Rupture Disc Rupture Indicator [Ex-ia] | IS_DI_NAMUR | 24VDC | TRUE | SIL-2 | CBL-202A | 3 | 0.45 | FALSE | BP-02-CH-07
PT-108-IS | Vent Header Pressure Transmitter [Zone 1] | IS_AI_HART | 24VDC | TRUE | SIL-2 | CBL-202A | 4 | 0.85 | FALSE | BP-02-CH-08
ZS-203-IS | Hydrocarbon Spill Sump High Level [Ex-ia] | IS_DI_NAMUR | 24VDC | TRUE | SIL-2 | CBL-203A | 1 | 0.45 | FALSE | BP-02-CH-09
ZS-204-IS | Vapor Recovery Unit Status [Ex-ia] | IS_DI_NAMUR | 24VDC | TRUE | SIL-2 | CBL-203A | 2 | 0.45 | FALSE | BP-02-CH-10
TT-401 | Turbine Bearing A Temperature Pt100 | RTD_PT100 | mV | FALSE | BPCS | CBL-301A | 1 | 0.35 | FALSE | BP-03-CH-01
TT-402 | Turbine Bearing B Temperature Pt100 | RTD_PT100 | mV | FALSE | BPCS | CBL-301A | 2 | 0.35 | FALSE | BP-03-CH-02
TT-403 | Compressor Thrust Bearing Temperature | RTD_PT100 | mV | FALSE | BPCS | CBL-301A | 3 | 0.35 | FALSE | BP-03-CH-03
TT-204 | Compressor Casing Temperature Sensor | RTD_PT100 | mV | FALSE | BPCS | CBL-301A | 4 | 0.35 | FALSE | BP-03-CH-04
TE-501 | Furnace Firebox Top Temp Thermocouple K | TC_TYPE_K | mV | FALSE | BPCS | CBL-302A | 1 | 0.25 | FALSE | BP-03-CH-05
TE-502 | Furnace Radiant Tube Wall Temperature | TC_TYPE_K | mV | FALSE | BPCS | CBL-302A | 2 | 0.25 | FALSE | BP-03-CH-06
TE-503 | Convection Section Flue Gas Temperature | TC_TYPE_K | mV | FALSE | BPCS | CBL-302A | 3 | 0.25 | FALSE | BP-03-CH-07
TT-404 | Cooling Water Return Temperature Pt100 | RTD_PT100 | mV | FALSE | BPCS | CBL-302A | 4 | 0.35 | FALSE | BP-03-CH-08
TT-405 | Lube Oil Sump Temperature Pt100 | RTD_PT100 | mV | FALSE | BPCS | CBL-303A | 1 | 0.35 | FALSE | BP-03-CH-09
TE-504 | Stack Flue Gas Emission Temperature | TC_TYPE_K | mV | FALSE | BPCS | CBL-303A | 2 | 0.25 | FALSE | BP-03-CH-10
TT-406 | Intercooler Outlet Gas Temp Pt100 | RTD_PT100 | mV | FALSE | BPCS | CBL-303A | 3 | 0.35 | FALSE | BP-03-CH-11
LSH-101 | Deethanizer Reboiler High Level Alarm Switch | DI_24V | 24VDC | FALSE | BPCS | CBL-401A | 1 | 0.5 | FALSE | BP-04-CH-01
LSL-101 | Deethanizer Reboiler Low Level Alarm Switch | DI_24V | 24VDC | FALSE | BPCS | CBL-401A | 2 | 0.5 | FALSE | BP-04-CH-02
ZSO-201 | ESD Feed Isolation Valve Open Limit Switch | DI_24V | 24VDC | FALSE | BPCS | CBL-401A | 3 | 0.5 | FALSE | BP-04-CH-03
ZSC-201 | ESD Feed Isolation Valve Closed Limit Switch | DI_24V | 24VDC | FALSE | BPCS | CBL-401A | 4 | 0.5 | FALSE | BP-04-CH-04
SOV-101 | ESD Emergency Feed Isolation Solenoid Valve | DO_24V | 24VDC | FALSE | BPCS | CBL-402A | 1 | 1.2 | FALSE | BP-04-CH-05
SOV-102 | Fuel Gas Emergency Vent Solenoid Valve | DO_24V | 24VDC | FALSE | BPCS | CBL-402A | 2 | 1.2 | FALSE | BP-04-CH-06
PMP-RUN-01 | Reflux Pump Motor Running Feedback Contact | DI_24V | 24VDC | FALSE | BPCS | CBL-402A | 3 | 0.5 | FALSE | BP-04-CH-07
PMP-CMD-01 | Reflux Pump Motor Remote Start Command DO | DO_24V | 24VDC | FALSE | BPCS | CBL-402A | 4 | 1.1 | FALSE | BP-04-CH-08
ALM-HORN-01 | Control Room Audible Annunciator Horn DO | DO_24V | 24VDC | FALSE | BPCS | CBL-403A | 1 | 1.1 | FALSE | BP-04-CH-09
ALM-STROBE-01 | Field Evacuation Strobe Beacon DO | DO_24V | 24VDC | FALSE | BPCS | CBL-403A | 2 | 1.1 | FALSE | BP-04-CH-10
ESD-PB-01 | Field Console Emergency Shutdown Pushbutton | DI_24V | 24VDC | FALSE | SIL-3 | CBL-403A | 3 | 0.5 | TRUE | BP-04-CH-11
ESD-RESET-01 | Field Safety Interlock Permissive Reset DI | DI_24V | 24VDC | FALSE | SIL-3 | CBL-403A | 4 | 0.5 | TRUE | BP-04-CH-12